## 01_Dashboard
SOLAR DESIGN ENGINEERING PACKAGE — DASHBOARD
Current Design |  | Design Status
Project | 44755 Savage Rd, Coarsegold CA | Electrical | PASS
Panel | REC Alpha Pure-RX 460 | Layout | Column-based strings
Inverter | Sol-Ark 18K-2P-LV | Shade | First-pass model
Battery | Discover Helios ESS | Cost | Hardware estimate only
Battery Qty | 3 | Mechanical | Engineer review required
Array Layout | 3×12 Portrait x1 Single Mount | Next Step | Validate rack height/wind loading
DC Array kW | 16.56
Battery Storage kWh | 48
Estimated Hardware $ | 45940
Electrical Status | PASS

## 02_Build
SOLAR DESIGN ENGINEERING PACKAGE — BUILD PAGE v4.0
Design Inputs |  | Selected Equipment Values |  | Live Engineering Summary |  | Check | Calculated | Limit | Status
Project | 44755 Savage Rd, Coarsegold CA | Panel W | 460 | Total Panels | 36 | String Vmp | 329.4 | 150–425 V | PASS
Panel Model | REC Alpha Pure-RX 460 | Panel Voc | 65.7 | DC Array kW | 16.56 | Cold Voc | 422.5824 | <500 V | PASS
Inverter | Sol-Ark 18K-2P-LV | Panel Vmp | 54.9 | String Vmp | 329.4 | MPPT Current | 16.76 | <36 A | PASS
Battery | Discover Helios ESS | Panel Isc | 8.88 | Cold String Voc | 422.5824 | MPPT Isc | 17.76 | <54 A | PASS
Battery Qty | 3 | Panel Imp | 8.38 | MPPT Operating Current | 16.76 | MPPT Count | 3 | <= 3 | PASS
Orientation | Portrait | Voc Temp %/C | -0.24 | MPPT Short-Circuit Current | 17.76
Mount Type | Single Mount | Panel Length ft | 5.6693 | Power per MPPT kW | 5.5207
Rows High | 3 | Panel Width ft | 3.9534 | Battery Storage kWh | 48
Columns Wide | 12 | Panel Cost | 315 | Estimated Hardware $ | 45940
Banks | 1 | Inv MPPT Min | 150 | Cost per DC Watt | 2.7742
Tilt ° | 37 | Inv MPPT Max | 425 | Panel Width ft | 3.9534
Azimuth ° | 180 | Inv Max Voc | 500 | Panel Length ft | 5.6693
Design Temp °C | -5 | Inv Max Op A | 36 | Array Width ft | 47.4409
Panels/String | 6 | Inv Max Isc A | 54 | Sloped Array Height ft | 17.0079
Total Strings | 6 | Inv MPPT Count | 3 | Ground Depth ft | 13.5831
Strings/MPPT | 2 | Inv Cost | 7900 | Rear Edge Rise ft | 10.2356
MPPT Mode | Manual | Battery kWh | 16 | Electrical Status | PASS
BOS Estimate $ | 12000 | Battery Cost | 4900 | Layout Note | Row spacing N/A - single structure
Visual Array Builder — default 3×12 column strings (change string IDs in cells)
S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
String | Physical Zone | MPPT | Shade Pairing Rationale
S1 | West edge columns 1-2 | MPPT1 | Pair west edge with east edge
S2 | West-center columns 3-4 | MPPT2 | Pair symmetric inward zones
S3 | Center-west columns 5-6 | MPPT3 | Pair center strings
S4 | Center-east columns 7-8 | MPPT3 | Pair center strings
S5 | East-center columns 9-10 | MPPT2 | Pair symmetric inward zones
S6 | East edge columns 11-12 | MPPT1 | Pair east edge with west edge
Design rationale: default strings are vertical column groups so east/west tree shadows tend to affect one string group at a time rather than clipping every row simultaneously. MPPT pairs are symmetric west/east to reduce the chance that a single edge shadow drags down both strings on the same tracker.

## 03_Layout_Designer
LAYOUT DESIGNER — Mechanical + Electrical Topology
Inputs linked from Build |  |  | Panel Map / String Topology
Orientation | Portrait |  | S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
Rows High | 3 |  | S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
Columns Wide | 12 |  | S1 | S1 | S2 | S2 | S3 | S3 | S4 | S4 | S5 | S5 | S6 | S6
Tilt ° | 37
Mount Type | Single Mount
Array Width ft | 47.4409
Sloped Height ft | 17.0079
Ground Depth ft | 13.5831
Rear Rise ft | 10.2356
Layout Comparisons
Option | Orientation | Rows | Cols | Panels | Width ft | Rear Rise ft | Ground Depth ft | String Fit | Notes
3×12 single mount | Portrait | 3 | 12 | 36 | 47.4409 | 10.2356 | 13.5831 | Clean 6 strings | Compact width; taller rear edge
3×12 single mount | Landscape | 3 | 12 | 36 | 68.0315 | 7.1377 | 9.472 | Clean 6 strings | Lower rear edge; wider footprint
2×18 single mount | Portrait | 2 | 18 | 36 | 71.1614 | 6.8237 | 9.0554 | Awkward with 6-panel column strings | Lower but wider; strings may traverse zones
2 banks of 2×9 | Portrait | 2 | 9 | 36 | 35.5807 | 6.8237 | 9.0554 | Likely awkward string crossing | Needs bank spacing; less desirable electrically

## 04_Shade_Optimizer
SHADE OPTIMIZER — First Iteration / Conceptual Model
Shade Inputs |  | String Impact Estimate
Time Scenario | Morning West Edge | String | Columns | Shade Hit? | Est Power % | Assigned MPPT
Shadowed Columns | 2 | S1 | 1-2 | YES | 15% | MPPT1
Power of shaded panel/string % | 15% | S2 | 3-4 | NO | 100% | MPPT2
Unshaded power % | 100% | S3 | 5-6 | NO | 100% | MPPT3
String strategy | Column Groups | S4 | 7-8 | NO | 100% | MPPT3
|  | S5 | 9-10 | NO | 100% | MPPT2
|  | S6 | 11-12 | NO | 100% | MPPT1
|  | MPPT | String A | String B | Avg Power % | Comment
|  | MPPT1 | S1 | S6 | 57.5% | Symmetric edge pairing
|  | MPPT2 | S2 | S5 | 100% | Symmetric mid pairing
|  | MPPT3 | S3 | S4 | 100% | Center pairing
This is a first-pass shade model. It is not a production simulator yet. Its purpose is to compare string topologies under edge-shadow behavior. Next iteration can add tree distance/height, solar azimuth, and a time slider.

## 05_Design_Review
DESIGN REVIEW CHECKLIST
Area | Check | Status | Notes
Electrical | String Vmp inside MPPT range | PASS
Electrical | Cold Voc below inverter max | PASS
Electrical | MPPT operating current below max | PASS
Electrical | MPPT Isc below max | PASS
Layout | Column-based strings selected | PASS | Chosen for east/west edge-shadow tolerance
Layout | 3×12 single mount under review | REVIEW | Verify rear-edge height/wind load with engineer
Battery | Battery integration | REVIEW | Confirm Discover/Sol-Ark firmware and wiring kit
Mechanical | Foundation/racking | REVIEW | Requires structural engineer
Site | Tree removal/shading | REVIEW | Measure tree heights and sun window after escrow

## DB_Panels
Manufacturer | Model | STC W | Voc V | Vmp V | Isc A | Imp A | Voc Temp %/C | Pmax Temp %/C | Length mm | Width mm | Weight lb | Series Fuse A | Max System V | Ballpark $/panel | Source/Notes
REC | REC Alpha Pure-RX 460 | 460 | 65.7 | 54.9 | 8.88 | 8.38 | -0.24 | -0.24 | 1728 | 1205 | 47.4 | 25 | 1000 | 315 | Verify against current REC datasheet before purchase
Qcells | Q.TRON BLK M-G2+ 430 | 430 | 45.54 | 38.39 | 11.35 | 11.2 | -0.24 | -0.29 | 1722 | 1134 | 48.5 | 25 | 1000 | 240 | Placeholder/current-market candidate; verify datasheet
Canadian Solar | HiKu6 455 | 455 | 49.3 | 41.5 | 11.74 | 10.97 | -0.26 | -0.34 | 1903 | 1134 | 54 | 25 | 1500 | 220 | Placeholder/current-market candidate; verify datasheet
Silfab | SIL-460/470 | 460 | 46.7 | 38.5 | 12.7 | 11.95 | -0.27 | -0.35 | 1909 | 1134 | 54 | 25 | 1000 | 280 | Placeholder; verify exact model
Trina | Vertex S+ 455 | 455 | 51.6 | 43.2 | 11.2 | 10.54 | -0.24 | -0.3 | 1762 | 1134 | 47 | 25 | 1500 | 210 | Placeholder; verify exact model

## DB_Inverters
Manufacturer | Model | MPPT Min V | MPPT Max V | PV Max Voc V | Max Operating A/MPPT | Max Isc A/MPPT | MPPT Count | Strings/MPPT | Max PV kW | AC Output kW | Ballpark $ | Notes
Sol-Ark | Sol-Ark 18K-2P-LV | 150 | 425 | 500 | 36 | 54 | 3 | 2 | 30 | 18 | 7900 | Use current Sol-Ark manual/datasheet for final design
Sol-Ark | Sol-Ark 15K | 175 | 425 | 500 | 26 | 44 | 3 | 2 | 19.5 | 15 | 6900 | Older/common baseline; verify manual

## DB_Batteries
Manufacturer | Model | Chemistry | Usable kWh | Nominal V | Capacity Ah | Cont Charge A | Cont Discharge A | Peak A | Weight lb | Closed Loop with Sol-Ark | Comm/Interface | Ballpark $/battery | Notes
Discover | Discover Helios ESS | LiFePO4 | 16 | 51.2 | 314 | 160 | 160 | 400 | 330 | Yes | Closed-loop / LYNK or native per current integration | 4900 | Preferred current candidate; verify integration kit/firmware
Pytes | Pytes V16 | LiFePO4 | 16 | 51.2 | 314 | 160 | 160 | 200 | 320 | Yes | CAN/RS485 | 3700 | Strong alternative; verify listing with installer
HomeGrid | Stack'd Series 19.2 | LiFePO4 | 19.2 | 51.2 | 375 | 200 | 200 | 300 | 500 | Yes | CAN/RS485 | 7200 | Expandable modular system
Fortress | eBoost 16 | LiFePO4 | 16 | 51.2 | 314 | 160 | 160 | 200 | 320 | Verify | CAN/RS485 | 5200 | Replacement direction for eVault; verify Sol-Ark closed loop

## DB_Lists
String IDs | Orientation | Mount Type | MPPT Mode | MPPT
S1 | Portrait | Single Mount | Manual | MPPT1
S2 | Landscape | Split Banks | Symmetric Pairing | MPPT2
S3 |  | Future |  | MPPT3
S4
S5
S6
Unassigned

## Notes
DESIGN NOTES / CHANGE LOG
Date/Version | Area | Decision | Rationale
v4.0 | Architecture | Build page redesigned as command center | User wants whole-picture design workflow instead of jumping across sheets
v4.0 | Layout | Default 3×12 single mount | Matches 36 panels, 6 strings, and compact footprint
v4.0 | Stringing | Default column-based strings | East/west shadows should affect one string group at a time
v4.0 | MPPT pairing | S1+S6, S2+S5, S3+S4 | Symmetric pairing balances edge-shade impacts
v4.0 | Equipment | Sol-Ark 18K + REC 460 + Discover Helios x3 | Clean voltage/current fit and battery integration candidate